## Heat Loss
ECONAR Energy Systems Corporation
Residential Heat Loss Calculation Worksheet
2015-01-15 15:08
Project Name: |  |  |  |  | Zone Name:
Prepared By: |  |  |  |  | Prepared For:
Approxmate Air Changes/Hour |  | 0.5 | Zone Length |  | Zone Width |  | Zone Height |  | Total Cubic or Square Feet
Air Infiltration Rate (CFM) |  | 96.192
Approximate Zone Volume 1 (cubic feet) |  |  | 60 | x | 24 | x | 8 | = | 11520
Approximate Zone Volume 2 (cubic feet) |  |  | 40 | x | 13 | x | 8 | = | 4160
Approximate Zone Volume 3 (cubic feet) |  |  | 20 | x | 21 | x | 9 | = | 3780
Approximate Zone Area 1 (square feet) |  |  | 60 | x | 24 | x |  | = | 1440
Approximate Zone Area 2 (square feet) |  |  | 40 | x | 13 | x |  | = | 520
Approximate Zone Area 3 (square feet) |  |  | 20 | x | 21 | x |  | = | 420
Approximate Exposed Wall Area 1 (square feet) |  |  | 168 | x |  | x | 8 |  | 1344
Approximate Exposed Wall Area 2 (square feet) |  |  | 106 | x |  | x | 8 |  | 848
Approximate Exposed Wall Area 3 (square feet) |  |  | 82 | x |  | x | 9 | = | 738
Indoor Dry-Bulb Design Temperature |  |  | 70 | Degrees Farenheit |  | Less Window Area: |  |  | 153
Outdoor Dry-Bulb Design Temperature |  |  | -15 | Degrees Farenheit |  | Less Door Area: |  |  | 120
Design Temperature Difference: |  |  | 85 |  |  | Actual Wall Area: |  |  | 2657
Structural Element | Structural Element Description |  | Area (square feet) |  | Element U-Value |  | Temperature Difference |  | Total BTUH
Above Grade Exterior Wall Info | 2 x 4 (R-13)+ |  |  | x | 0.071788 | x | 85 | = | 0
| 2 x 6 (R-19)+ |  | 1131 | x | 0.050176 | x | 85 | = | 4823.6327
| Other |  | 312 | x | 0.0502 | x | 85 | = | 1331.304
Window Information | Single Pane |  |  | x | 0.55098 | x | 85 | = | 0
| Double Pane |  | 153 | x | 0.40511 | x | 85 | = | 5268.4637
| Deluxe with Storm |  |  | x | 0.36823 | x | 85 | = | 0
| Other |  |  | x |  | x | 85 | = | 0
Exterior Door Information | Solid-Core Wood |  |  | x | 0.25251 | x | 85 | = | 0
| 1-3/4" 24 ga. Steel |  | 120 | x | 0.16863 | x | 85 | = | 1720.0675
| 1-3/4" 18 ga. Steel |  |  | x | 0.22573 | x | 85 | = | 0
| Other |  |  | x |  | x | 85 | = | 0
Roof/Ceiling Information | R-38+ |  |  | x | 0.025687 | x | 85 | = | 0
| R-40+ |  |  | x | 0.024432 | x | 85 | = | 0
| R-42+ |  | 1440 | x | 0.023294 | x | 85 | = | 2851.1529
| R-44+ |  |  | x | 0.022257 | x | 85 | = | 0
| Other |  |  | x |  | x | 85 | = | 0
Above Grade Exposed Floor (crawlspace) | 2 x 8 (R-24)+ |  |  | x | 0.040112 | x | 85 | = | 0
| 2 x 10 (R-28)+ |  |  | x | 0.034566 | x | 85 | = | 0
| 2 x 12 (R-33)+ |  |  | x | 0.029472 | x | 85 | = | 0
| Other |  |  | x |  | x | 85 | = | 0
Cement Slab | Slab on Grade |  |  | x | 0.063776 | x | 85 | = | 0
Structural Element | Structural Element Description |  | Area (square feet) |  | BTUH Loss Factor
Below Grade Elements | Floor |  | 1440 | x | 3 | BTUH per Sq. Ft. |  | = | 4320
| Walls |  | 992 | x | 6 | BTUH per Sq. Ft. |  | = | 5952
Air Losses | Air Loss Description |  | Air CFM |  | Loss Factor |  | Temperature Difference
| Infiltration |  | 96.192 | x | 1.1 | x | 85 | = | 8993.952
| Ventilation & Make-Up |  |  | x | 1.1 | x | 85 | = | 0
Duct Loss | Is ductwork in an unconditioned space? |  | Yes / No |  | HL Factor |  | Subtotal | = | 35260.5727
|  |  | No |  | 0 | x | 35260.5727 | = | 0
[7 empty] | Total Heat Loss: |  | 35260.5727
("+" Indicates inside and outside air film is calculated in U-Value)
(U-Value = 1 / R-Value = BTUH / Square Feet / Degree Farenheit Temperature Design)
(Air Loss Factor = BTUH / CFM / Degree Farenheit Temperature Design) | [8 empty] | Rev. 12-31-14
Note on C15: The user enters this value based on the formula below: NAC = (Target (post) Blower Door Reading x 60) / (17 x Volume) Natural Air Changes per Hour (NAC)
Note on C16: This number is calculated by the formula above.
Note on D17: The user enters these above-grade values.
Note on F17: The user enters these above-grade values.
Note on H17: The user enters these above-grade values.
Note on D20: The values in the cells above are automatically entered in these cells.
Note on F20: The values in the cells above are automatically entered in these cells.
Note on D23: These are calculated fields. example: =(2*D17)+(2*F17)
Note on H23: The values in the cells above are automatically entered in these cells.
Note on D26: Indoor Dry-Bulb Design Temperature *** The user enters this value *** This is the indoor ambient air temperature, which the furnace can heat the house to. Average is 75-76 degrees.
Note on J26: The user enters this value, which is the total window area from below (Window Information).
Note on D27: *** The user enters this value *** This information comes from Manual J, Eighth Edition, Addendum E - Weather Data Values http://www.acca.org/other-standard/addendum-e-manual-j-weather-data/
Note on J27: The user enters this value, which is the total door area from below (Exterior Door Information).
Note on D30: User enters values below.
Note on H30: The Design Temperature Difference is automatically entered into the cells below.
Note on F34: User enters this value. (see below to determine U-Value)
Note on F38: User enters this value. (see below to determine U-Value)
Note on F42: User enters this value. (see below to determine U-Value)
Note on F47: User enters this value. (see below to determine U-Value)
Note on F51: User enters this value. (see below to determine U-Value)
Note on D53: User enters values below.
Note on H57: This value is automatically inserted from above (design temperature difference).
Note on D59: This value is automatically inserted from above (air infiltration rate).
Note on D60: User enters this value which is the recommended continuous ventilation according to ASHRAE recommendation or ERV, if one was installed.
Note on D61: User enters the value below.